## Metadata
Title | Power Grid Integration Performance Report
Author | Vijay Kumar Singh
Date | 2026-06-18
Abstract | This technical report evaluates the dynamic stability and power grid integration parameters for the primary utility inverter bank. Measurements were acquired via ETAP simulation and related transient run routines under step-load conditions.
Methodology | A 60-second operational run was conducted at a sampling interval of 10 seconds. Active power levels, system frequency, grid bus voltage, and inverter core temperature were monitored for safety limit violations.

## Summary
Parameter | Measured | Units | Limit | Status | Conclusion
Active Power Output | 45.2 | kW | >40 | PASS | Normal grid feed-in.
Grid Frequency | 50.05 | Hz | 49.5-50.5 | PASS | Frequency stable within statutory limits.
Bus Voltage | 412.3 | V | 380-420 | PASS | Voltage profile stable.
Inverter Temperature | 78.4 | C | <80 | WARNING | Inverter core temperature is near warning limit.
Total Harmonic Distortion | 3.1 | % | <5 | PASS | Harmonic content complies with IEEE-519.

## TimeSeries
Time | Active Power Output | Grid Frequency | Bus Voltage | Inverter Temperature
0 | 40.1 | 50.01 | 410.2 | 70
10 | 42.5 | 50.02 | 411 | 72.5
20 | 44.8 | 50.04 | 411.8 | 75.1
30 | 45.2 | 50.05 | 412.3 | 78.4
40 | 43.9 | 50.03 | 411.5 | 77.2
50 | 42.1 | 50.02 | 410.8 | 76
60 | 40.5 | 50.01 | 410.3 | 74.5